## Sheet1 (hidden)
| CUSTOMER : MOTORES Y ENERGIA S.A.S. |  |  |  | Frame | Cable size (Home) | Cable size (Export)
| INDENT NO : 0413703967/2200 |  |  |  | ND100L | 1 * 3C,6-MM² | 2 * 3C,6-MM²
| PO NO : 000IMP0008 |  |  |  | ND112M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
CROMPTON GREAVES LTD. | PO DATE : 09/01/2014 |  |  |  | ND132M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
LT MOTORS DIVISION | DATE : 10/05/2016 |  |  |  | ND132S | 1 * 3C,10-MM² | 1 * 3C,10-MM²
AHMEDNAGAR |  |  |  |  | ND160L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
TAG NO | , |  | SAP Database |  | ND160M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
QUANTITY | 1 | SAP | QUANTITY |  | ND180L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
DRIVEN EQUIPMENT | As Per Customer | SAP | DIRRTN |  | ND180M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
DUTY | S1 | SAP | DUTY |  | ND200L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
MANUFACTURER | CROMPTON GREAVES LTD. | CROMPTON GREAVES LTD. |  |  | ND225M | 2 * 3C,50-MM² | 2 * 3C,120-MM²
TYPE | 3 PHASE AC SQUIRREL CAGE INDUCTION MOTOR IE2 | 3PHASE, AC INDUCTION MOTOR |  |  | ND225S | 2 * 3C,50-MM² | 2 * 3C,120-MM²
FRAME DESIGNATION | ND200L | SAP | FRAME | 200 | ND250M | 2 * 3C,70-MM² | 2 * 3C,120-MM²
OUTPUT ---- KW | 18.5 | SAP | KW |  | ND250MX | 2 * 3C,70-MM² | 2 * 3C,120-MM²
VOLTAGE ----- VOLT | 220D/380S/440D | SAP | VOLTAGE |  | ND280M | 2 * 3C,95-MM² | 2 * 3C,120-MM²
FULL LOAD CURRENT----- AMP | 64D/37S/32D | #VALUE! |  |  | ND280S | 2 * 3C,95-MM² | 2 * 3C,120-MM²
FULL LOAD SPEED ---- RPM | 1170 | SAP |  |  | ND315L | 2 * 3C,150-MM² | 2 * 3C,150-MM²
ENCLOSURE | TEFC Safe Area | LOGIC |  |  | ND315LX | 2 * 3C,150-MM² | 2 * 3C,150-MM²
TYPE OF PROTECTION | IP55 | SAP | DP |  | ND315M | 2 * 3C,150-MM² | 2 * 3C,150-MM²
GAS GROUP | NOT APPLICABLE | IF BLANK THEN PRINT NOT APPLICABLE ELSE SAP VALUE |  |  | ND315S | 2 * 3C,150-MM² | 2 * 3C,150-MM²
MOUNTING | B3 | SAP | MTG |  | ND355L | 2 * 3C,240-MM² | 2 * 3C,240-MM²
AMB. TEMP/TEMP RISE ---- °C | 40°C/80°C (BY RESISTANCE METHOD) | SAP | AMB/TRISE (BY RESISTANCE METHOD) |  | ND355LX | 2 * 3C,240-MM² | 2 * 3C,240-MM²
FULL LOAD TORQUE ----- KGM | 15.4009 | #VALUE! |  |  | ND400LX | 2 * 3C,400-MM² | 2 * 3C,400-MM²
APPLICABLE CODE | IEC 60034, | SAP | STD |  | ND450LX | 4 * 3C,300-MM² | 4 * 3C,300-MM²
STARTING TORQUE AS --- %FLT | 200 | SAP | STG_TORQUE |  | ND80 | 1 * 3C,6-MM² | 1 * 3C,6-MM²
%EFF @100% LOAD | 91.7 | SAP | FLEFF |  | ND90L | 2 * 3C,6-MM² | 2 * 3C,6-MM²
%EFF @75% LOAD | 91.7 | SAP | EFF34FL |  | ND90S | 2 * 3C,6-MM² | 2 * 3C,6-MM²
%EFF @50% LOAD | 90 | SAP | EFF12FL |  | E80 | 1 * 3C,6-MM² | 1 * 3C,6-MM²
ROTATION VIEWED FROM DE | Clockwise from DE | SAP | DIRRTN |  | E90L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
BEARING TYPE --- DE/ODE | 6312-ZZ/6212-ZZ | SAP | BRG_TYPE |  | E100L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
TYPE OF LUBRICATION | Greased for life | SAP | LUB_TYPE |  | E112M | 1 * 3C,6-MM² | 1 * 3C,6-MM²
NET WEIGHT (APPR.) --- KG | 252 | SAP | ZFRMWEIGHT |  | E132M | 1 * 3C,6-MM² | 1 * 3C,6-MM²
TYPE OF COUPLING | Not Specified | SAP | COUPLING |  | E160L | 1 * 3C,25-MM² | 1 * 3C,25-MM²
CABLE SIZE TYPE --- mm. sq | STANDARD,STANDARD | SAP | CABLE_SIZE | 2 * 3C,25-MM² | E180L | 1 * 3C,25-MM² | 1 * 3C,25-MM²
PHASE/CONN/NO OF TERMINAL | 3/Delta/6 | SAP | PHASE | 2 * 3C,25-MM² | E200L | 1 * 3C,25-MM² | 1 * 3C,25-MM²
FREQUENCY ---- Hz | 60.0,+-5% | SAP | FREQUENCY |  | E225S | 1 * 3C,50-MM² | 1 * 3C,50-MM²
INSULATION CLASS | F (Temp. rise limited to class ‘B’) | SAP | INSL |  | E225M | 1 * 3C,50-MM² | 1 * 3C,50-MM²
No. OF POLES | 6 | SAP | POLE |  | E250M | 1 * 3C,70-MM² | 1 * 3C,70-MM²
LOCKED ROTOR CURRENT %FLC | 600 | SAP | SCC_COMM |  | E280M | 1 * 3C,95-MM² | 1 * 3C,95-MM²
LR WITHSTD TIME HOT/COLD | 12/24. | SAP | LRTIME_HOT/LRTIME_COL |  | E315M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
STATOR THERMAL TIME CONST MIN | 45 | SAP | STTIME_CNT | 90 | E315L | 2 * 3C,185-MM² | 2 * 3C,185-MM²
PF @-100% LOAD | 0.84 | SAP | FLPF |  | E355LX | 2 * 3C,240-MM² | 2 * 3C,240-MM²
PF @ 75% LOAD | 0.82 | SAP | PF34FL |  | GD63S | 1 * 3C,6-MM² | 1 * 3C,6-MM²
PF @- 50% LOAD | 0.7 | SAP | PF12FL |  | GD71S | 1 * 3C,6-MM² | 1 * 3C,6-MM²
PULL OUT TORQUE --- %FLT | 250 | SAP | POT_FLT |  | GD80M | 1 * 3C,6-MM² | 1 * 3C,6-MM²
SPACE HEATERS - WATTS/VOLTS | N.A. | SAP | SPACE_HEAT/240 V |  | GD90S | 1 * 3C,6-MM² | 1 * 3C,6-MM²
ACCESSORIES | N.A. | SAP | ACCES |  | GD90L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
PAINT SHADE | RAL5021EPOXY(WATER BLUE) | SAP | PAINT |  | GD100L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
TB POSITION FROM DE | TOP | SAP | TBPOS |  | GD112M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
Load GD SQ. (KG-M²) | 2.29 | FROM SAP . IF NOT MAINTAINED , = MOTOR GD² | GD2 |  | GD132S | 1 * 3C,10-MM² | 1 * 3C,10-MM²
MOTOR GD SQ. (KG-M²) | 2.29 | SAP | MOTOR_GD2 |  | GD132M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
STARTING TIME @100% V SEC |  | FROM ACCESS TABLE |  |  | NG80 | 1 * 3C,6-MM² | 2 * 3C,6-MM²
TYPE OF STARTING | Direct On Line | SAP | STG |  | NG90S | 1 * 3C,6-MM² | 1 * 3C,6-MM²
NOISE LEVEL | As per IEC60034-9 | SAP | NOISE |  | NG90L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
VIBRATION | As per IEC 60034-14 | SAP | VIBRN |  | NG100L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | NG112M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | NG132S | 1 * 3C,10-MM² | 1 * 3C,10-MM²
NOTE : 1) ALL PERFORMANCE FIGURES ARE SUBJECT TO IS 325 - 1996 TOLERANCES . |  |  |  |  | NG132M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
2) FOR INVERTER DRIVEN MOTORS, MAX. ALLOWED %THD FOR VOLTAGE = 3% |  |  |  |  | ND250S | 2 * 3C,70-MM² | 2 * 3C,70-MM²
AND TEMPERATURE RISE IS LIMITED TO CLASS F LIMITS |  |  |  |  | ND355S | 2 * 3C,240-MM² | 2 * 3C,240-MM²
3) FOR INVERTER DRIVEN MOTORS, VOLTAGE SPIKES ARE ALLOWED MAXIMUM 1600 V |  |  |  |  | ND355M | 2 * 3C,240-MM² | 2 * 3C,240-MM²
AND MIN. RISE TIME OF 0.1 MICROSECOND. CABLE LENGTH TO BE SELECTED ACCORDINGLY. |  |  |  |  | PC100L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
ISSUED BY : | Prashant Pujari |  |  |  | PC80 | 1 * 3C,6-MM² | 1 * 3C,6-MM²
| LT MOTORS DIVISION , AHMEDNAGAR |  |  |  | PC90L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | PC90S | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | PC132S | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | PC132M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | PC112M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | PA100L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | PA112M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | PA132M | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | PA132S | 1 * 3C,10-MM² | 1 * 3C,10-MM²
[5 empty] | PA90L | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | PA90S | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | PA80 | 1 * 3C,6-MM² | 1 * 3C,6-MM²
[5 empty] | PC160M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | PC160L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | PC180M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | PC180L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | PC200L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | PC225S | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | PC225M | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | PC250S | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | PC250M | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | PC280S | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | PC280M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | PC315S | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | PC315M | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | PC315L | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | PC355L | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | NDW225M | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | NDW225S | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | NDW250M | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | NDW250S | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | NDW280M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | NDW280S | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | NDW315L | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | NDW315LX | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | NDW315M | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | NDW315S | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | NDW355L | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | NDW355LX | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | NDW355M | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | NDW355S | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | NDW400LX | 2 * 3C,400-MM² | 2 * 3C,400-MM²
[5 empty] | NDW160L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | NDW160M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | CW225M | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | CW250S | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | CW250M | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | CW250MX | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | CW280S | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | CW280M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | CW280MX | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | CW160M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | CW160ML | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | CW180M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | CW180L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | CW200M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | CW200L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | NDW250MX | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | CW315M | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | CW315MX | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | CW315S | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | CW355L | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | CW355M | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | EW250M | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | EW280M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | EW315M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | DW132M | 2 * 3C,10-MM² | 2 * 3C,10-MM²
Standard bearings | 6312-ZZ/6212-ZZ |  |  |  | DW132S | 2 * 3C,10-MM² | 2 * 3C,10-MM²
FLP | No |  |  |  | NDW112M | 2 * 3C,10-MM² | 2 * 3C,10-MM²
Possibility of providing roller at DE | Yes |  |  |  | NDW180L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
Roller applicable | No |  |  |  | NDW200L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
Roller bearings DE | NU312-C3 |  |  |  | NR160L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
Roller bearings ODE | 6312-C3 |  |  |  | NR160M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
Roller bearing string | NU312-C3/6312-C3 |  |  |  | NR180L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
Insulated brg |  |  |  |  | NR180M | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | NR200L | 2 * 3C,25-MM² | 2 * 3C,25-MM²
[5 empty] | NR225M | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | NR225S | 2 * 3C,50-MM² | 2 * 3C,50-MM²
[5 empty] | NR250MX | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | NR250M | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | NR250S | 2 * 3C,70-MM² | 2 * 3C,70-MM²
[5 empty] | NR280M | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | NR280S | 2 * 3C,95-MM² | 2 * 3C,95-MM²
[5 empty] | NR315M | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | NR315S | 2 * 3C,150-MM² | 2 * 3C,150-MM²
[5 empty] | NR315L | 2 * 3C,240-MM² | 2 * 3C,240-MM²
[5 empty] | GD80 | 1 * 3C,6-MM² | 1 * 3C,6-MM²

## Datasheet
INDENT NO : 0413703967/2200
PO NO : 000IMP0008
CROMPTON GREAVES LTD. | PO DATE : 09/01/2014
LT MOTORS DIVISION | DATE : 10/05/2016
AHMEDNAGAR
SAP Database
QUANTITY | 1 | SAP | QUANTITY
DRIVEN EQUIPMENT | As Per Customer | SAP | DIRRTN
DUTY | S1 | SAP | DUTY
MANUFACTURER | CROMPTON GREAVES LTD. | CROMPTON GREAVES LTD.
TYPE | 3 PHASE AC SQUIRREL CAGE INDUCTION MOTOR IE2 | 3PHASE, AC INDUCTION MOTOR
FRAME DESIGNATION | ND200L | SAP | FRAME
OUTPUT ---- KW | 18.5 | SAP | KW
No. OF POLES | 6
VOLTAGE ----- VOLT | 220D/380S/440D | SAP | VOLTAGE
FULL LOAD CURRENT----- AMP | 64D/37S/32D | #VALUE!
FULL LOAD SPEED ---- RPM | 1170 | SAP
ENCLOSURE | TEFC Safe Area | LOGIC
TYPE OF PROTECTION | IP55 | SAP | DP
GAS GROUP | NOT APPLICABLE | IF BLANK THEN PRINT NOT APPLICABLE ELSE SAP VALUE
MOUNTING | B3 | SAP | MTG
AMB. TEMP/TEMP RISE ---- °C | 40°C/80°C (BY RESISTANCE METHOD) | SAP | AMB/TRISE (BY RESISTANCE METHOD)
FULL LOAD TORQUE ----- KGM | 15.4009 | #VALUE!
APPLICABLE CODE | IEC 60034, | SAP | STD
STARTING TORQUE AS --- %FLT | 200 | SAP | STG_TORQUE
PULL OUT TORQUE --- %FLT | 250
%EFF @100% LOAD | 91.7 | SAP | FLEFF
%EFF @75% LOAD | 91.7 | SAP | EFF34FL
%EFF @50% LOAD | 90 | SAP | EFF12FL
PF @-100% LOAD | 0.84
PF @ 75% LOAD | 0.82
PF @- 50% LOAD | 0.7
ROTATION VIEWED FROM DE | Clockwise from DE | SAP | DIRRTN
BEARING TYPE --- DE/ODE | 6312-ZZ/6212-ZZ | SAP | BRG_TYPE
TYPE OF LUBRICATION | Greased for life | SAP | LUB_TYPE
NET WEIGHT (APPR.) --- KG | 252 | SAP | ZFRMWEIGHT
TYPE OF COUPLING | Not Specified | SAP | COUPLING
CABLE SIZE TYPE --- mm. sq | 2 * 3C,25-MM² | SAP | CABLE_SIZE
PHASE/CONN/NO OF TERMINAL | 3/Delta/6 | SAP | PHASE
FREQUENCY ---- Hz | 60.0,+-5% | SAP | FREQUENCY
INSULATION CLASS | F (Temp. rise limited to class ‘B’) | SAP | INSL
LOCKED ROTOR CURRENT %FLC | 600 | SAP | SCC_COMM
LR WITHSTD TIME HOT/COLD | 12/24. | SAP | LRTIME_HOT/LRTIME_COL
STATOR THERMAL / COOLING TIME CONST MIN | 45/90 | SAP | STTIME_CNT
SPACE HEATERS - WATTS/VOLTS | N.A. | SAP | SPACE_HEAT/240 V
ACCESSORIES | N.A. | SAP | ACCES
PAINT SHADE | RAL5021EPOXY(WATER BLUE) | SAP | PAINT
TB POSITION FROM DE | TOP | SAP | TBPOS
Load GD SQ. (KG-M²) | 2.29 | FROM SAP . IF NOT MAINTAINED , = MOTOR GD² | GD2
MOTOR GD SQ. (KG-M²) | 2.29 | SAP | MOTOR_GD2
STARTING TIME @100% V SEC | 0.8 | FROM ACCESS TABLE
TYPE OF STARTING | Direct On Line | SAP | STG
NOISE LEVEL | As per IEC60034-9 | SAP | NOISE
VIBRATION | As per IEC 60034-14 | SAP | VIBRN
RV/RA | 0 | 0.7732
NOTE : 1) ALL PERFORMANCE FIGURES ARE SUBJECT TO IS 325 - 1996 TOLERANCES .
2) FOR INVERTER DRIVEN MOTORS, MAX. ALLOWED %THD FOR VOLTAGE = 3%
AND TEMPERATURE RISE IS LIMITED TO CLASS F LIMITS
3) FOR INVERTER DRIVEN MOTORS, VOLTAGE SPIKES ARE ALLOWED MAXIMUM 1600 V
AND MIN. RISE TIME OF 0.1 MICROSECOND. CABLE LENGTH TO BE SELECTED ACCORDINGLY.
ISSUED BY : | Prashant Pujari
LT MOTORS DIVISION , AHMEDNAGAR